## Preliminaries
PROPOSED BOREHOLE REHABILITATION WORKS
LOCATION:MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
ITEM | DESCRIPTION | UNIT | QTY. | RATE (USD) | AMOUNT (USD)
A | Mobilization
1 | Allow a provisonal sum for equipment and tools mobilization. | Lumpsum | 1 |  | 0
2 | Allow a provisional sum for staff and techncial personell. | Lumpsum | 1 |  | 0
3 | Allow a provisional sum for camp/site demobilization | Lumpsum | 1 |  | 0
4 | Allow a provisional sum for reqired water & power on site during project life. | Lumpsum | 1 |  | 0
| Total amount carried to summary page |  |  |  | 0

## New elevated water tank
PROJECT: BOREHOLE SUPPORT INFRASTRUCTURES WORKS
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
Elevated Water Tank 40m3 (12m high)
Item | Description | Unit | Qty | Rate ($) | Amount($)
1 | Foundation
1.11 | Excavation: General excavation works for the column's foundations, depth up to 1500mm in all type of soil | m3 | 39.89 |  | 0
1.12 | Lean concrete (2000 x 2000mm, thickness 50mm): lean concrete, mix 1:4:8, ready to receive the the column's foundations | m3 | 1.2 |  | 0
1.13 | Foundations (1400 x 1400mm, thickness 600mm): reinforced concrete class 20 (nominal mix 1:2:4) with Y12 at column bases | m3 | 7.056 |  | 0
2 | Columns and Beams
2.11 | Columns (section: 300mmx 300mm): reinforced concrete mix 1:2:4, with high yield twisted rebar of Y12 and R6 for stirrups @200mm c/c | m3 | 5.83 |  | 0
2.15 | Beam (section 300x450mm), concrete class 20,nominal mix 1:2:4) with Y16 rebar and R8 for beam links | m3 | 9.32 |  | 0
3 | Storage tank (RC slabs and RC walls)
3.11 | Tank slab: (3400 x 6400mm, thickness 1500mm): reinforced concrete class 25 ( nominal mix 1:2:3) complete with water proofing, 12mm dia high yield square twisted bars for tank base slab | m3 | 3.264 |  | 0
3.13 | Water bar: 200mm water bar | Lm | 17 |  | 0
3.14 | Walls: (thickness 12mm and height of 2000mm) reinforced concrete class 25 ( nominal mix 1:2:3) complete with water proofing; 12mm high yield square twisted bars for tank walls | m3 | 3.384 |  | 0
3.16 | Cover slab: (4400 x 4400mm, thickness 150mm): reinforced concrete class 20 (nominal mix 1:2:4), 12mm high yield square twisted bars for tank cover slab | m3 | 1.984 |  | 0
4 | Inspection manhole and fittings
4.11 | Inspection manhole (600mm x 600mm): Reinforced concrete 50mm thick with BS mesh A142, bent up round iron bars handle and 50x50x3mm, using of Y12 HY Square twisted bars at man hole corners | unit | 0.02 |  | 0
4.13 | BS mesh A142 for manhole cover | m2 | 0.4 |  | 0
4.14 | 50x50x3mm L angle plates | lm | 16 |  | 0
4.15 | Fittings: supply and install all fittings for inlet, distribution and trucking outlets and overflow | LS | 1 |  | 0
4.16 | Ladder (500mm width,13m length): Supply and install a metallic ladder, including all anchorage points | unit | 1 |  | 0
Total |  |  |  |  | 0

## Borehole supplies
PROPOSED BOREHOLE SUPPLIES
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
No. | Description | Unit | Qty | Unit Costs | Total
1 | Submersible pump, Grundfos SP17-20 Rp2 with 11kw motor, with matching cut-off electrodes, drop cables control panel, all accessories included | Pcs | 1 |  | 0
2 | Provision and installation of 3'' riser main pipe for the borehole with complete fittings | Pcs | 25 |  | 0
3 | Gate valves and control pannel for the pump | Pcs | 1 |  | 0
4 | Allow a provisonal sum for piping from the borehole to the elevated tank at the borehole site inclusive of excavation works | Item | 1 |  | 0
5 | 30KVA Duos Genset, in-line direct injection 3-cylinder diesel engine/ type water cooled of four cycle | No | 1 |  | 0
6 | Allow a proviosional sum of water meter readers in the borehole outlet | No. | 1 |  | 0
7 | Allow provisonal sum of gantry at borehole site | No | 1 |  | 0
| TOTAL |  |  |  | 0
| SUBTOTAL CARRIED TO MAIN SUMMARY |  |  |  | 0

## Distribution Piping
PROPOSED PIPING WORKS - 1,000 METRES
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
ITEM | DESCRIPTION | UNIT | QTY. | RATE (USD) | AMOUNT (USD)
A | Trench excavation and pipe laying
1 | Excavation of a trench (0.4m wide x 0.6m deep) for a total length of 1000m from borehole to the water kiosk | m3 | 240 |  | 0
2 | Install 2" uPVC pressure pipes including all necessary fittings from borehole to the school, installed over a sand bed 7 cm thick and covered with sand for a minimum thickness of 10 cm. | M.L. | 1000 |  | 0
3 | Refill the pipeline trench with duly compacted soil free of relicts of excavation | M.L. | 1000 |  | 0
4 | Demarcation and layouts preparation | LS | 1 |  | 0
5 | Construction of chamber control Box (50x50x50cm) | Sum | 6 |  | 0
6 | Testing the system | Sum | 1 |  | 0
| Sub-total: Trenches and laying of Pipes |  |  |  | 0
B | Supply of pipes,fittings & other items
1 | Supply of 2 inch uPVC pressure pipes for supplying water from tank to the water kiosks | Pcs | 166.6667 |  | 0
2 | Supply of all the fittings including elbows, tees, unions, gate valves, flow meters etc | Pcs | 40 |  | 0
| Sub-total: Pipes and fittings |  |  |  | 0
SUMMARY
A | Trenches and Laying of Pipes |  |  |  | 0
B | Supply of pipes and fittings |  |  |  | 0
| Grand Total: Installation of 1,000meters Water Distribution Pipeline |  |  |  | 0

## Solar Support Structure
PROJECT: PROPOSED BOREHOLE REHABILITATION WORKS
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
ITEM | DESCRIPTION |  | UNIT | QNTY | RATE US$ | AMT US$
MOUNTING SUPPORT STEEL STRUCTURE
ELEMENT NO. 1 : SITE PREPARATION
A | Clear site of all bushes and debris. Grab up roots and |  | m2 | 24 |  | 0
burn the arisings
B | Load, wheel and cart deposit and spread surplus excavated
material where directed on site at a distance not exceeding
| 100 meters |  | Item | 1 |  | 0
| Total carried to summary |  | $ |  |  | 0
ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL)
Excavations including maintaining and supporting sides
and keeping free from water, mud and fallen material
A | Top soil excavation average 200mm deep |  | m3 | 4.8 |  | 0
B | Excavate for foundation not exceeding 0.3
| meters deep, starting from stripped levels |  | m3 | 0.48 |  | 0
| Extra over for excavation in rock |  | m3 | 7.2 |  | 0
Ditto
C | Column bases |  | m3 | 1.62 |  | 0
Planking and strutting
D | Allow for keeping foundations free from water, mud, fallen
| materials, etc. |  | LS | 1 |  | 0
Disposal
E | Return, fill and ram selected excavated material around
| foundations |  | m3 | 0.486 |  | 0
F | Load, wheel and cart deposit and spread surplus
excavated material where directed on site at a
| distance not exceeding 100 meters |  | m3 | 1.134 |  | 0
Hardcore or other approved filling, as described
G | 300mm thick well compacted hardcore filling blinded with
| 25mm thick quarry dust layer to receive surface bed |  | m2 | 1.44 |  | 0
H | 50mm thick Quarry dust blinding to surfaces of hardcore :rolled |  | m2 | 15 |  | 0
smooth to receive polytheen sheeting (m.s)
Anti-termite treatment
I | Gladiator or equal and approved chemical anti-termite
treatment, executed complete by an approved specialist
| under a ten-year guarantee, to surfaces of blinding |  | m2 | 15 |  | 0
Damp-proof membrane
I | 1000 gauge polythene or other equal and approved
damp-proof membrane, laid over blinded hardcore
(m.s) with 300mm side and end laps (measured
| nett-allow for laps) |  | m2 | 15 |  | 0
| Total carried to summary |  | $ |  |  | 0
ELEMENT NO. 3 : STEEL FRAME
Assemble all materials and construct a steel frame to support
solar panels. The contrator is reminded to cost all materials
labour: cutting, hoisting, placing welding, bolting priming with red oxide,
painting and fixing of panels on the structure
A | 50mm dia. GI pipes forming framework as described
Columns
| 1500mm height |  | No. | 22.5 |  | 0
Beams
| 4700mm length |  | No. | 28.2 |  | 0
| 2500mm length |  | No. | 25 |  | 0
B | 50mm x 3mm thick steel angle bars
Supports
| 2.5m length |  | No. | 30 |  | 0
| 800mm bracings |  | No. | 16 |  | 0
| Total carried to summary |  | $ |  |  | 0
ELEMENT NO. 4 : CONCRETE WORKS
Plain concrete class 15 in:
A | 100mm blinding |  | m3 | 1.5 |  | 0
B | Ditto for column bases |  | m3 | 0.135 |  | 0
Insitu concrete class 25/20 , vibrated and reinforced with 60mm thick
maximum aggregate size in as described, in:-
SLABS
C | 200mm thick surface bed laid in bays including all
| necessary formwork |  | m3 | 3.6 |  | 0
Ditto:
D | Suspended slab |  | m3 | 3.6 |  | 0
E | Roof slab |  | m3 | 3.6 |  | 0
| Total carried to summary |  | $ |  |  | 0
ELEMENT NO. 5 : FINISHES
A | Cement and sand (1:3) screeds, backings, beds etc
25mm Thick cement/sand (1:4) screed finish
| Floor slab |  | m2 | 18 |  | 0
Painting
B | Prepare surfaces and apply three coats gloss oil paint as 'Crown'
or equal and approved manufacturer(s) on concrete and masonry
surfaces: measured overall on both sides
| Plastered surfaces internally and externally |  | LS | 1 |  | 0
| Total carried to summary |  | $ |  |  | 0
MAIN SUMMARY
| No. | ELEMENT |  | PAGE
| 1 | ELEMENT NO. 1 : SITE PREPARATION |  | 5/1 |  | 0
| 2 | ELEMENT NO. 2 : SUBSTRUCTURES (PROVISIONAL) |  | 5/2 |  | 0
| 6 | ELEMENT NO. 3 : STEEL FRAME |  | 5/6 |  | 0
| 8 | ELEMENT NO. 4 : CONCRETE WORKS |  | 5/8 |  | 0
| 9 | ELEMENT NO. 5 : FINISHES |  | 5/9 |  | 0
| Grand Total |  |  |  |  | 0
| Total for THREE No. mounting structures |  |  |  |  | 0
| TOTAL FOR SECTION 5: CARRIED TO GRAND SUMMARY |  |  |  |  | 0

## Solar Installation
PROJECT: PROPOSED BOREHOLE REHABILITATION WORKS
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
ITEM | DESCRIPTION | UNIT | QNTY | RATE US$ | AMT US$
SOLAR PROCUREMENT,DELIVERY & INSTALLATION
1 | Procurement and delivery of 350 watts Jinko solar panels | No | 60 |  | 0
2 | 8mm2 submersible pump 3-phase motor cable | Meter | 190 |  | 0
3 | Supply and installation of Well probe sensor c/w cable for dry running protection | Meter | 180 |  | 0
4 | Supply and installation of manual change over switch to switch between solar and generator power | No. | 1 |  | 0
5 | Supply and installation of PSk2-15 Controller-11kVA-D | No. | 1 |  | 0
6 | Supply and installation of PV Disconnect Switch 1000V-40-6 | No. | 1 |  | 0
7 | Supply and installation of PV Protect 125A | No. | 2 |  | 0
8 | Supply and installation of PV Combiner 1000-125-4 | No. | 2 |  | 0
9 | Supply and installation of Surge Protector | No. | 1 |  | 0
10 | Accessories | Lot | 1 |  | 0
11 | Installation of 60 solar panels on already fabricated steel support strauctures | Lot | 1 |  | 0
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  | 0

## Fencing works
ITEM | DESCRIPTION |  | UNIT | QNTY | RATE US$ | AMT US$
PROJECT: PROPOSED BOREHOLE REHABILITATION WORKS
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
SECTION 8: FENCE AND GATE
ELEMENT No. 1: GATE
The contractor will provide all material and construct a steel
gate maesuring approximately 4000x2100m.
Given the location and site conditions, the contractor is
advised to make a physical assesment of the site before
tendering.
A | Excavate for column pads, depth not exceeding
1.5m and of 1.5 x 1.5 mm width commencing at the original
| ground level, and cart away to spoil as directed |  | CM | 6.75 |  | 0
Reinforced Concrete using 3/4 + 1/2" mix machine
crushed Ballast in:
B | Vibrated reinforced concrete (class 25) column base, 350mm deep |  | CM | 0.7875 |  | 0
C | Ditto in columns 600x600mm thick, average height of 2.7 m
| with 1.5 m being the foundation column |  | CM | 1.944 |  | 0
D | Assorted high tensile twisted steel reinforcement bars to B.S 4446. |  | KG | 200 |  | 0
E | Sawn formwork to vertical sides of the columns |  | SM | 10 |  | 0
F | 15mm thick cement/Sand plaster to vertical sides of the columns |  | SM | 10 |  | 0
G | 350x350x25mm thick P.C.C coping stone |  | No | 2 |  | 0
Main and pedestrian gates
H | Supply and fix double leaf steel gate size 4000x 2100mm high
CHS poleswith small pedestrian door made from 2"x 3mm thick
welded on one side of the frame. Frame as follows: 75 x 3mm
thick RHS external members and 25mm SHS 3mm thick secondary
members, fixed onto the concrete columns using heavy duty steel
pin hinges; with all fastening accessories including all cutting
welding, grinding and priming with one coat of grey oxide before
fixing. The gate should also have peep holes of not more that
25mm dia with a slilding door. It should also have 2 locking
| mechanisms, top and bottom. |  | NO | 1 |  | 0
| Sub-Total for main and pestrian gate |  |  |  |  | 0
PROJECT: PROPOSED BOREHOLE REHABILITATION WORKS
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
SECTION 8: FENCE AND GATE
ELEMENT No. 2 : FENCE
The contractor is reminded to include in his pricing,
the cost of supply, cutting, waste and erection and all other
necessary fittings including welding lugs or fishtailing onto
the 50x50x6mm angle bars. Angle bars and the necessary
fixing and anchorage to be treated as described in the
specifications.
Fence construction should be according to BS 1722-Part 10
A | Clear the perimeter of the fencing area of all bushes scrubs and obstructions |  | SM | 96 |  | 0
B | Excavate 300x300x500 deep holes to receive mass concrete (1:3:6)
| bases as shown in the drawings. |  | CM | 2.4 |  | 0
C | Supply 50x5mm CHS welded to form Y-shaped posts with ends closed as
shown in the drawings, bottom end fixed with 100x100mmx3mm plate
and bedded in mass concrete.The post to be 2500mm high from ground
| level to the Y-joint. Allow for drlling 7No holes as shown. |  | NO | 53.3333 |  | 0
D | Extra Over 50x5mm posts for bracing on either side every fourth
| intermediate post and all corner posts. |  | NO | 13.3333 |  | 0
Mass Concrete Mix 1:3:6/20mm using 3/4 Local Ballast in:
E | Supply all materials and cast 0.3m diameter x 0.6m depth mass concrete
class Q (1:3:6) to concrete the 50mm dia. CHS poles while ensuring they
remain plumb 600mm deep below the ground level and 2500mm (2.5m)
| above ground level. |  | CM | 2.4 |  | 0
F | Supply and weld a 12mm high tensile steel rod along the bases of the posts
for anchoring the chainlink to the ground along the whole length of the fence.
| Allow for excavating 200mm deep along the fence to fix the rod. |  | LM | 160 |  | 0
G | Allow for curing of all concrete works |  | Item | 1 |  | 0
H | Supply and fix 3No strands of 12G barbed wire bound onto either sides
| of the Y post using 3mm galvanised wire as shown in the drawings. |  | LM | 960 |  | 0
I | Ditto for posts |  | LM | 1120 |  | 0
J | Supply and and fix 2500mm high HEAVY GUAGE chainlink to posts using 3mm
galvanised wire. Allow for securing the chainlink to a 12mm reinforcement
| bar welded at the base btween the posts. |  | LM | 160 |  | 0
K | Supply and fix razer wire secured on the chainlink, barbed wire and Y posts
| by binding wire and rolled approximately 600mm dia. |  | LM | 160 |  | 0
L | Prepare and apply one under coat of epoxy based primer and two finishing
| epoxy based paints to metal surfaces n.e 250mm in alternate bands of 300mm |  | No. | 66.6667 |  | 0
| Total carried to summary |  |  |  |  | 0
PROJECT: PROPOSED BOREHOLE REHABILITATION WORKS
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
SECTION 8: FENCE AND GATE
ELEMENT NO. 3 : MAIN SUMMARY
| ELEMENT No. | TITLE |  | PAGE |  | Amount
| 1 | ELEMENT No. 1: GATE |  | 1/2 |  | 0
| 2 | ELEMENT No. 2 : FENCE |  | 2/2 |  | 0
| Total |  |  |  |  | 0
| Total carried to grand summary |  |  |  |  | 0

## Summary
PROJECT: PROPOSED BOREHOLE REHABILITATION WORKS
LOCATION: MA XUMAADE VILLAGE BOREHOLE XARARDHEERE DISTRICT
COST SUMMARY
1 | Preliminaries | 1 | 0
2 | New elevated water tank | 1 | 0
3 | Borehole Supplies | 1 | 0
4 | Distribution piping network | 1 | 0
5 | Solar Support Structure | 1 | 0
6 | Solar Installation | 1 | 0
7 | Fencing works | 1 | 0
| TOTAL |  | 0
| GRAND TOTAL |  | 0