## Guriel Airport
BILLS OF QUANTITIES
PROPOSED INSTALATION OF SOLAR ENERGY AT GURIEL AIRPORT MIDAS WORKSTATION (15KW)
ITEM | DESCRIPTION | UNIT | QTY
A | PV Mounting structure: Supply and install Module mounting structure from Galvanized Steel structures to fix the photovoltaic panels. The structure must be suitable to the dimension of selected PV modules and PV numbers, the mounting provides a fixed inclination of the modules 30 degree with vertical supports, plates, the structure profile includes bracing and double hot galvanized angles for dividers.The mounting structures and the foundations must be designed structurally to be suitable to withstand all static loads (weight of modules, wind loads etc) that might occur according to the Site conditions. The mounting structure components are bonded together to guaranty potential equalization. All works and materials must be according to drawings, specifications and supervisor instructions and approval. | L.S | 1
B | PV Modules – 15 kWp: MONO-si SOLAR CELL, 540W Supply, install, connect and operate Mono Crystalline Solar Modules, - Maximum Power/Pmax (W): 540 9 Module Type KT-540M-144 - Maximum Power Tolerence: 0-3% - Optimum Operation Volatage/Vmp (V): 41.64 - Open Operation Current/Imp (A): 12.97 - Open-Circuit Volatage/Voc (V): 49.60 - Short-Circuit Current/ isc (A): 13.93 - Power Specifications at STC:1000W/m2, AM1.5 CELL25C - Net Weight (KG): 28.6 - Max system Voltage (V): 1500V - Cell Technology: MONO-si - Module Application Class: A All material needed to have complete job ready for installing high quality PV modules with total arrays capacity to achieve 10KWp. The item Includes supply, install & connect the following: • Water proof PV junction boxes for each array including DC Fuses, DC switch disconnectors, bus bars ,terminals, ducts or trays, supports & labels suitable to the PV arrays loads. • Solar DC cables appropriately sized to connect the PV solar cells together and to the inverter directly to have a complete operational circuit with all conduits, clamps , trays and cable end terminations which shall be DC plug and socket connectors . The DC cables must be sized in accordance with the installation requirements applicable on site, the allowable voltage drop for DC cables between PV Arrays and inverter less than 1%. • The price includes all works, making good and reinstatement including necessary materials and workmanship as well as removal of unwanted materials to dump sites approved by the engineer to complete the job successfully. • Contractor must submit all the required certificates for each PV solar panel from. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 30
C | Inverters – 20 KW: (Model M5000h-48BP PV Off-Grid Inverter) Supply, install, connect and operate DC/AC offgrid tie 3-phase inverter with data communication and energy meter with following specification: Inverter Mode - Battery Input: 48VDC, 117A - Type of Battery: Lead Acid/ Lithium - Rated Power: 5000VA/5000W - AC Output: 230VAC,50/60Hz, 40A, 1dim - AC Input: 230VAC,50/60Hz, 40A, 1dim - Max AC charge Current 80Amp - Max. PV Input Voltage (VOC): 450VDC - Max. PV Input Current 18A - MPPT Volatage Range: 120, 430VDC - Max. Charge Current 100A - Coomunication: WIFI/GPSRS (Option) The inverterwith must be suited to any PV module configuration, and depending on the system design and installation proposed and for the future extended also. (Model M5000h-48BP PV Off-Grid Inverter). The DC max power input rating should be equal or more than 20KW of the PV modules capacity at standard test condition. The inverter unit shall be suitable with weather condition as indoor installations. The inverters AC nominal power output rating must be equal or greater than 5KW to be total of 20KWp compatible with the AC loads design. The inverter must include the safety concepts such as (triple protection with optiprotect, electronic strings fuses, self-learning string failure detection, DC surge arrestor type 2 ) to ensure max availability. The price includes : • Supply, install and connect (monitoring and controlling unit) for all PV solar system installed especially compatible with the inverters, with all needed accessories, interface modules & data cables and all connections needed to complete and connect the monitoring system to internet. • Supply , install and connect all DC cables appropriately sized in accordance with the installation requirements and to connect the inverters with PV system designed with all conduits, clamps, trays and cable terminations end which shall be DC plug and socket connectors to have a complete job, the allowable voltage drop for DC cables between inverters and PV system not less than 1%. • Inverters shall allow an adjustable power factor minimum AC output power with all necessary electrical cables, earthing system, Conduits, trays and all other materials and workmanship needed to connect with the main distribution panel according to the engineer's instruction and approval and have a complete job. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 4
D | Battery Bank: Supply, install, connect and operate Lithium Ion Battery with following specifications: - Normal volt (V): GBP480 - Normal capacity: (AH) 100 - Working volt range: 42-56.25 - Recommend charging volt (V): 52.5 - Recommending discharging cutoff volt (V): 45 - Standard charging current (A): 50 - Max. Discharging current (A): 100 - Protection: IP20 - Max Dimension (W*D*H) for rack typr: 482.6*535*175 - Net Weight: 56kg The batteries must provide high-quality and achieving superior performance, the manufacturing date must be new and not more than 6 months, suitable for every type of applications especially for solar renewable energy, designed Service Life 10 years with low internal resistance, designed to be deeply discharged. The Battery should provide benefits of being maintenance free, case flame retardant & non-hazardous. The price Includes supply, install & connect Battery temp. sensor (BTS) and the following: • All necessary DC cables between the batteries together and to the battery fuse box to have a complete operational circuit with all bus bars, conduits, clamps, stainless steel bolts, washers and cable end terminations and all needed materials to complete the job. All DC cables must be sized in accordance with the installation requirements applicable on site ,the allowable voltage drop must be less than 1%. • Battery Banks rack from the same manufacturer of the batteries with dividers and all needed accessories to finish the job. the rack must be enough to carry all the weight of the required batteries for the system. • The contractor must submit manufacturer warranty for each battery cell for a period 10 years. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 4
E | Battery Rack : (Wall Mounting) Batteries shall be installed in clean, dry locations. They must be secured against falling items and dirt, The battery racks will be built in parallel connected racks using the battery distribution panel that's according to mounting circuit diagram.The battery is designed and built in conformity with the latest technical rules at the time of its development and production, so it is safe to operate. Danger maybe presented by the battery, if it will is used for other than the intended purpose and by unskilled personnel. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 2
F | CABLES AND ACCESSORIES DC cables 8mm x 500m, surge protectors, Combination boxes, MCB, Fuses, MC4 Connectors core cable from luminay to battery. 2 core cable from Panel to battery. nominal cross sectional area of conductor 50sq mm wire for battery connections. Assorted nuts and bolts for panel fixing. Lugs for wires. Battery rack from metal , Allow for all necessary AC wiring connections of 10mm x 1,500 meter from the power source (Solar) to the All workstations including fixing, distribution boards, sockets and trucking pipes, AC circuit breakers for each MIDAS Station, as directed on the site specifications and supervisor instructions approval. | Set | 1
J | Construction of Storage Room (3x4m) Supply and construct 3x4m Room to store batteries and solar inverters, Room shall be equiped with one A/C 9000BTU, Room shall have two windows and a door, floorbed should be suitable to withstand batteries wieght and shall have tiles. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | Lumps | 1
H | Installation, Testing and Commissioning | Lumps | 1
I | Transport and logistics | Lumps | 1

## Abudwak Airport
BILLS OF QUANTITIES
PROPOSED INSTALATION OF SOLAR ENERGY AT ABUDWAK AIRPORT MIDAS WORKSTATION (15KW)
ITEM | DESCRIPTION | UNIT | QTY
A | PV Mounting structure: Supply and install Module mounting structure from Galvanized Steel structures to fix the photovoltaic panels. The structure must be suitable to the dimension of selected PV modules and PV numbers, the mounting provides a fixed inclination of the modules 30 degree with vertical supports, plates, the structure profile includes bracing and double hot galvanized angles for dividers.The mounting structures and the foundations must be designed structurally to be suitable to withstand all static loads (weight of modules, wind loads etc) that might occur according to the Site conditions. The mounting structure components are bonded together to guaranty potential equalization. All works and materials must be according to drawings, specifications and supervisor instructions and approval. | L.S | 1
B | PV Modules – 15 kWp: MONO-si SOLAR CELL, 540W Supply, install, connect and operate Mono Crystalline Solar Modules, - Maximum Power/Pmax (W): 540 9 Module Type KT-540M-144 - Maximum Power Tolerence: 0-3% - Optimum Operation Volatage/Vmp (V): 41.64 - Open Operation Current/Imp (A): 12.97 - Open-Circuit Volatage/Voc (V): 49.60 - Short-Circuit Current/ isc (A): 13.93 - Power Specifications at STC:1000W/m2, AM1.5 CELL25C - Net Weight (KG): 28.6 - Max system Voltage (V): 1500V - Cell Technology: MONO-si - Module Application Class: A All material needed to have complete job ready for installing high quality PV modules with total arrays capacity to achieve 10KWp. The item Includes supply, install & connect the following: • Water proof PV junction boxes for each array including DC Fuses, DC switch disconnectors, bus bars ,terminals, ducts or trays, supports & labels suitable to the PV arrays loads. • Solar DC cables appropriately sized to connect the PV solar cells together and to the inverter directly to have a complete operational circuit with all conduits, clamps , trays and cable end terminations which shall be DC plug and socket connectors . The DC cables must be sized in accordance with the installation requirements applicable on site, the allowable voltage drop for DC cables between PV Arrays and inverter less than 1%. • The price includes all works, making good and reinstatement including necessary materials and workmanship as well as removal of unwanted materials to dump sites approved by the engineer to complete the job successfully. • Contractor must submit all the required certificates for each PV solar panel from. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 30
C | Inverters – 20 KW: (Model M5000h-48BP PV Off-Grid Inverter) Supply, install, connect and operate DC/AC offgrid tie 3-phase inverter with data communication and energy meter with following specification: Inverter Mode - Battery Input: 48VDC, 117A - Type of Battery: Lead Acid/ Lithium - Rated Power: 5000VA/5000W - AC Output: 230VAC,50/60Hz, 40A, 1dim - AC Input: 230VAC,50/60Hz, 40A, 1dim - Max AC charge Current 80Amp - Max. PV Input Voltage (VOC): 450VDC - Max. PV Input Current 18A - MPPT Volatage Range: 120, 430VDC - Max. Charge Current 100A - Coomunication: WIFI/GPSRS (Option) The inverterwith must be suited to any PV module configuration, and depending on the system design and installation proposed and for the future extended also. (Model M5000h-48BP PV Off-Grid Inverter). The DC max power input rating should be equal or more than 20KW of the PV modules capacity at standard test condition. The inverter unit shall be suitable with weather condition as indoor installations. The inverters AC nominal power output rating must be equal or greater than 5KW to be total of 20KWp compatible with the AC loads design. The inverter must include the safety concepts such as (triple protection with optiprotect, electronic strings fuses, self-learning string failure detection, DC surge arrestor type 2 ) to ensure max availability. The price includes : • Supply, install and connect (monitoring and controlling unit) for all PV solar system installed especially compatible with the inverters, with all needed accessories, interface modules & data cables and all connections needed to complete and connect the monitoring system to internet. • Supply , install and connect all DC cables appropriately sized in accordance with the installation requirements and to connect the inverters with PV system designed with all conduits, clamps, trays and cable terminations end which shall be DC plug and socket connectors to have a complete job, the allowable voltage drop for DC cables between inverters and PV system not less than 1%. • Inverters shall allow an adjustable power factor minimum AC output power with all necessary electrical cables, earthing system, Conduits, trays and all other materials and workmanship needed to connect with the main distribution panel according to the engineer's instruction and approval and have a complete job. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 4
D | Battery Bank: Supply, install, connect and operate Lithium Ion Battery with following specifications: - Normal volt (V): GBP480 - Normal capacity: (AH) 100 - Working volt range: 42-56.25 - Recommend charging volt (V): 52.5 - Recommending discharging cutoff volt (V): 45 - Standard charging current (A): 50 - Max. Discharging current (A): 100 - Protection: IP20 - Max Dimension (W*D*H) for rack typr: 482.6*535*175 - Net Weight: 56kg The batteries must provide high-quality and achieving superior performance, the manufacturing date must be new and not more than 6 months, suitable for every type of applications especially for solar renewable energy, designed Service Life 10 years with low internal resistance, designed to be deeply discharged. The Battery should provide benefits of being maintenance free, case flame retardant & non-hazardous. The price Includes supply, install & connect Battery temp. sensor (BTS) and the following: • All necessary DC cables between the batteries together and to the battery fuse box to have a complete operational circuit with all bus bars, conduits, clamps, stainless steel bolts, washers and cable end terminations and all needed materials to complete the job. All DC cables must be sized in accordance with the installation requirements applicable on site ,the allowable voltage drop must be less than 1%. • Battery Banks rack from the same manufacturer of the batteries with dividers and all needed accessories to finish the job. the rack must be enough to carry all the weight of the required batteries for the system. • The contractor must submit manufacturer warranty for each battery cell for a period 10 years. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 4
E | Battery Rack : (Wall Mounting) Batteries shall be installed in clean, dry locations. They must be secured against falling items and dirt, The battery racks will be built in parallel connected racks using the battery distribution panel that's according to mounting circuit diagram.The battery is designed and built in conformity with the latest technical rules at the time of its development and production, so it is safe to operate. Danger maybe presented by the battery, if it will is used for other than the intended purpose and by unskilled personnel. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 2
F | CABLES AND ACCESSORIES DC cables 8mm x 500m, surge protectors, Combination boxes, MCB, Fuses, MC4 Connectors core cable from luminay to battery. 2 core cable from Panel to battery. nominal cross sectional area of conductor 50sq mm wire for battery connections. Assorted nuts and bolts for panel fixing. Lugs for wires. Battery rack from metal , Allow for all necessary AC wiring connections of 10mm x 1,500 meter from the power source (Solar) to the All workstations including fixing, distribution boards, sockets and trucking pipes, AC circuit breakers for each MIDAS Station, as directed on the site specifications and supervisor instructions approval. | Set | 1
J | Construction of Storage Room (3x4m) Supply and construct 3x4m Room to store batteries and solar inverters, Room shall be equiped with one A/C 9000BTU, Room shall have two windows and a door, floorbed should be suitable to withstand batteries wieght and shall have tiles. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | Lumps | 1
H | Installation, Testing and Commissioning | Lumps | 1
I | Transport and logistics | Lumps | 1

## Ferfer Land Border
BILLS OF QUANTITIES
PROPOSED INSTALATION OF SOLAR ENERGY AT FER-FER LAND BORDER MIDAS WORKSTATION (10KW)
ITEM | DESCRIPTION | UNIT | QTY
A | PV Mounting structure: Supply and install Module mounting structure from Galvanized Steel structures to fix the photovoltaic panels. The structure must be suitable to the dimension of selected PV modules and PV numbers, the mounting provides a fixed inclination of the modules 30 degree with vertical supports, plates, the structure profile includes bracing and double hot galvanized angles for dividers.The mounting structures and the foundations must be designed structurally to be suitable to withstand all static loads (weight of modules, wind loads etc) that might occur according to the Site conditions. The mounting structure components are bonded together to guaranty potential equalization. All works and materials must be according to drawings, specifications and supervisor instructions and approval. | L.S | 1
B | PV Modules – 10 kWp: MONO-si SOLAR CELL, 540W Supply, install, connect and operate Mono Crystalline Solar Modules, - Maximum Power/Pmax (W): 540 9 Module Type KT-540M-144 - Maximum Power Tolerence: 0-3% - Optimum Operation Volatage/Vmp (V): 41.64 - Open Operation Current/Imp (A): 12.97 - Open-Circuit Volatage/Voc (V): 49.60 - Short-Circuit Current/ isc (A): 13.93 - Power Specifications at STC:1000W/m2, AM1.5 CELL25C - Net Weight (KG): 28.6 - Max system Voltage (V): 1500V - Cell Technology: MONO-si - Module Application Class: A All material needed to have complete job ready for installing high quality PV modules with total arrays capacity to achieve 10KWp. The item Includes supply, install & connect the following: • Water proof PV junction boxes for each array including DC Fuses, DC switch disconnectors, bus bars ,terminals, ducts or trays, supports & labels suitable to the PV arrays loads. • Solar DC cables appropriately sized to connect the PV solar cells together and to the inverter directly to have a complete operational circuit with all conduits, clamps , trays and cable end terminations which shall be DC plug and socket connectors . The DC cables must be sized in accordance with the installation requirements applicable on site, the allowable voltage drop for DC cables between PV Arrays and inverter less than 1%. • The price includes all works, making good and reinstatement including necessary materials and workmanship as well as removal of unwanted materials to dump sites approved by the engineer to complete the job successfully. • Contractor must submit all the required certificates for each PV solar panel from. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 20
C | Inverters – 15 KW: (Model M5000h-48BP PV Off-Grid Inverter) Supply, install, connect and operate DC/AC offgrid tie 3-phase inverter with data communication and energy meter with following specification: Inverter Mode - Battery Input: 48VDC, 117A - Type of Battery: Lead Acid/ Lithium - Rated Power: 5000VA/5000W - AC Output: 230VAC,50/60Hz, 40A, 1dim - AC Input: 230VAC,50/60Hz, 40A, 1dim - Max AC charge Current 80Amp - Max. PV Input Voltage (VOC): 450VDC - Max. PV Input Current 18A - MPPT Volatage Range: 120, 430VDC - Max. Charge Current 100A - Coomunication: WIFI/GPSRS (Option) The inverterwith must be suited to any PV module configuration, and depending on the system design and installation proposed and for the future extended also. (Model M5000h-48BP PV Off-Grid Inverter). The DC max power input rating should be equal or more than 15KW of the PV modules capacity at standard test condition. The inverter unit shall be suitable with weather condition as indoor installations. The inverters AC nominal power output rating must be equal or greater than 5KW to be total of 15KWp compatible with the AC loads design. The inverter must include the safety concepts such as (triple protection with optiprotect, electronic strings fuses, self-learning string failure detection, DC surge arrestor type 2 ) to ensure max availability. The price includes : • Supply, install and connect (monitoring and controlling unit) for all PV solar system installed especially compatible with the inverters, with all needed accessories, interface modules & data cables and all connections needed to complete and connect the monitoring system to internet. • Supply , install and connect all DC cables appropriately sized in accordance with the installation requirements and to connect the inverters with PV system designed with all conduits, clamps, trays and cable terminations end which shall be DC plug and socket connectors to have a complete job, the allowable voltage drop for DC cables between inverters and PV system not less than 1%. • Inverters shall allow an adjustable power factor minimum AC output power with all necessary electrical cables, earthing system, Conduits, trays and all other materials and workmanship needed to connect with the main distribution panel according to the engineer's instruction and approval and have a complete job. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 3
D | Battery Bank: Supply, install, connect and operate Lithium Ion Battery with following specifications: - Normal volt (V): GBP480 - Normal capacity: (AH) 100 - Working volt range: 42-56.25 - Recommend charging volt (V): 52.5 - Recommending discharging cutoff volt (V): 45 - Standard charging current (A): 50 - Max. Discharging current (A): 100 - Protection: IP20 - Max Dimension (W*D*H) for rack typr: 482.6*535*175 - Net Weight: 56kg The batteries must provide high-quality and achieving superior performance, the manufacturing date must be new and not more than 6 months, suitable for every type of applications especially for solar renewable energy, designed Service Life 10 years with low internal resistance, designed to be deeply discharged. The Battery should provide benefits of being maintenance free, case flame retardant & non-hazardous. The price Includes supply, install & connect Battery temp. sensor (BTS) and the following: • All necessary DC cables between the batteries together and to the battery fuse box to have a complete operational circuit with all bus bars, conduits, clamps, stainless steel bolts, washers and cable end terminations and all needed materials to complete the job. All DC cables must be sized in accordance with the installation requirements applicable on site ,the allowable voltage drop must be less than 1%. • Battery Banks rack from the same manufacturer of the batteries with dividers and all needed accessories to finish the job. the rack must be enough to carry all the weight of the required batteries for the system. • The contractor must submit manufacturer warranty for each battery cell for a period 10 years. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 3
E | Battery Rack : (Wall Mounting) Batteries shall be installed in clean, dry locations. They must be secured against falling items and dirt, The battery racks will be built in parallel connected racks using the battery distribution panel that's according to mounting circuit diagram.The battery is designed and built in conformity with the latest technical rules at the time of its development and production, so it is safe to operate. Danger maybe presented by the battery, if it will is used for other than the intended purpose and by unskilled personnel. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 3
F | CABLES AND ACCESSORIES DC cables 8mm x 500m, surge protectors, Combination boxes, MCB, Fuses, MC4 Connectors core cable from luminay to battery. 2 core cable from Panel to battery. nominal cross sectional area of conductor 50sq mm wire for battery connections. Assorted nuts and bolts for panel fixing. Lugs for wires. Battery rack from metal , Allow for all necessary AC wiring connections of 10mm x 1,500 meter from the power source (Solar) to the All workstations including fixing, distribution boards, sockets and trucking pipes, AC circuit breakers for each MIDAS Station, as directed on the site specifications and supervisor instructions approval. | Set | 1
J | Construction of Storage Room (3x4m) Supply and construct 3x4m Room to store batteries and solar inverters, Room shall be equiped with one A/C 9000BTU, Room shall have two windows and a door, floorbed should be suitable to withstand batteries wieght and shall have tiles. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | Lumps | 1
H | Installation, Testing and Commissioning | Lumps | 1
I | Transport and logistics | Lumps | 1

## Balambale Land Border
BILLS OF QUANTITIES
PROPOSED INSTALATION OF SOLAR ENERGY AT BALAN BALE LAND BORDER MIDAS WORKSTATION (10KW)
ITEM | DESCRIPTION | UNIT | QTY
A | PV Mounting structure: Supply and install Module mounting structure from Galvanized Steel structures to fix the photovoltaic panels. The structure must be suitable to the dimension of selected PV modules and PV numbers, the mounting provides a fixed inclination of the modules 30 degree with vertical supports, plates, the structure profile includes bracing and double hot galvanized angles for dividers.The mounting structures and the foundations must be designed structurally to be suitable to withstand all static loads (weight of modules, wind loads etc) that might occur according to the Site conditions. The mounting structure components are bonded together to guaranty potential equalization. All works and materials must be according to drawings, specifications and supervisor instructions and approval. | L.S | 1
B | PV Modules – 10 kWp: MONO-si SOLAR CELL, 540W Supply, install, connect and operate Mono Crystalline Solar Modules, - Maximum Power/Pmax (W): 540 9 Module Type KT-540M-144 - Maximum Power Tolerence: 0-3% - Optimum Operation Volatage/Vmp (V): 41.64 - Open Operation Current/Imp (A): 12.97 - Open-Circuit Volatage/Voc (V): 49.60 - Short-Circuit Current/ isc (A): 13.93 - Power Specifications at STC:1000W/m2, AM1.5 CELL25C - Net Weight (KG): 28.6 - Max system Voltage (V): 1500V - Cell Technology: MONO-si - Module Application Class: A All material needed to have complete job ready for installing high quality PV modules with total arrays capacity to achieve 10KWp. The item Includes supply, install & connect the following: • Water proof PV junction boxes for each array including DC Fuses, DC switch disconnectors, bus bars ,terminals, ducts or trays, supports & labels suitable to the PV arrays loads. • Solar DC cables appropriately sized to connect the PV solar cells together and to the inverter directly to have a complete operational circuit with all conduits, clamps , trays and cable end terminations which shall be DC plug and socket connectors . The DC cables must be sized in accordance with the installation requirements applicable on site, the allowable voltage drop for DC cables between PV Arrays and inverter less than 1%. • The price includes all works, making good and reinstatement including necessary materials and workmanship as well as removal of unwanted materials to dump sites approved by the engineer to complete the job successfully. • Contractor must submit all the required certificates for each PV solar panel from. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 20
C | Inverters – 15 KW: (Model M5000h-48BP PV Off-Grid Inverter) Supply, install, connect and operate DC/AC offgrid tie 3-phase inverter with data communication and energy meter with following specification: Inverter Mode - Battery Input: 48VDC, 117A - Type of Battery: Lead Acid/ Lithium - Rated Power: 5000VA/5000W - AC Output: 230VAC,50/60Hz, 40A, 1dim - AC Input: 230VAC,50/60Hz, 40A, 1dim - Max AC charge Current 80Amp - Max. PV Input Voltage (VOC): 450VDC - Max. PV Input Current 18A - MPPT Volatage Range: 120, 430VDC - Max. Charge Current 100A - Coomunication: WIFI/GPSRS (Option) The inverterwith must be suited to any PV module configuration, and depending on the system design and installation proposed and for the future extended also. (Model M5000h-48BP PV Off-Grid Inverter). The DC max power input rating should be equal or more than 15KW of the PV modules capacity at standard test condition. The inverter unit shall be suitable with weather condition as indoor installations. The inverters AC nominal power output rating must be equal or greater than 5KW to be total of 15KWp compatible with the AC loads design. The inverter must include the safety concepts such as (triple protection with optiprotect, electronic strings fuses, self-learning string failure detection, DC surge arrestor type 2 ) to ensure max availability. The price includes : • Supply, install and connect (monitoring and controlling unit) for all PV solar system installed especially compatible with the inverters, with all needed accessories, interface modules & data cables and all connections needed to complete and connect the monitoring system to internet. • Supply , install and connect all DC cables appropriately sized in accordance with the installation requirements and to connect the inverters with PV system designed with all conduits, clamps, trays and cable terminations end which shall be DC plug and socket connectors to have a complete job, the allowable voltage drop for DC cables between inverters and PV system not less than 1%. • Inverters shall allow an adjustable power factor minimum AC output power with all necessary electrical cables, earthing system, Conduits, trays and all other materials and workmanship needed to connect with the main distribution panel according to the engineer's instruction and approval and have a complete job. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 3
D | Battery Bank: Supply, install, connect and operate Lithium Ion Battery with following specifications: - Normal volt (V): GBP480 - Normal capacity: (AH) 100 - Working volt range: 42-56.25 - Recommend charging volt (V): 52.5 - Recommending discharging cutoff volt (V): 45 - Standard charging current (A): 50 - Max. Discharging current (A): 100 - Protection: IP20 - Max Dimension (W*D*H) for rack typr: 482.6*535*175 - Net Weight: 56kg The batteries must provide high-quality and achieving superior performance, the manufacturing date must be new and not more than 6 months, suitable for every type of applications especially for solar renewable energy, designed Service Life 10 years with low internal resistance, designed to be deeply discharged. The Battery should provide benefits of being maintenance free, case flame retardant & non-hazardous. The price Includes supply, install & connect Battery temp. sensor (BTS) and the following: • All necessary DC cables between the batteries together and to the battery fuse box to have a complete operational circuit with all bus bars, conduits, clamps, stainless steel bolts, washers and cable end terminations and all needed materials to complete the job. All DC cables must be sized in accordance with the installation requirements applicable on site ,the allowable voltage drop must be less than 1%. • Battery Banks rack from the same manufacturer of the batteries with dividers and all needed accessories to finish the job. the rack must be enough to carry all the weight of the required batteries for the system. • The contractor must submit manufacturer warranty for each battery cell for a period 10 years. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 3
E | Battery Rack : (Wall Mounting) Batteries shall be installed in clean, dry locations. They must be secured against falling items and dirt, The battery racks will be built in parallel connected racks using the battery distribution panel that's according to mounting circuit diagram.The battery is designed and built in conformity with the latest technical rules at the time of its development and production, so it is safe to operate. Danger maybe presented by the battery, if it will is used for other than the intended purpose and by unskilled personnel. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | UNIT | 3
F | CABLES AND ACCESSORIES DC cables 8mm x 500m, surge protectors, Combination boxes, MCB, Fuses, MC4 Connectors core cable from luminay to battery. 2 core cable from Panel to battery. nominal cross sectional area of conductor 50sq mm wire for battery connections. Assorted nuts and bolts for panel fixing. Lugs for wires. Battery rack from metal , Allow for all necessary AC wiring connections of 10mm x 1,500 meter from the power source (Solar) to the All workstations including fixing, distribution boards, sockets and trucking pipes, AC circuit breakers for each MIDAS Station, as directed on the site specifications and supervisor instructions approval. | Set | 1
J | Construction of Storage Room (3x4m) Supply and construct 3x4m Room to store batteries and solar inverters, Room shall be equiped with one A/C 9000BTU, Room shall have two windows and a door, floorbed should be suitable to withstand batteries wieght and shall have tiles. All works and materials must be according to the drawings, specifications and supervisor engineer instruction’s and approval. | Lumps | 1
H | Installation, Testing and Commissioning | Lumps | 1
I | Transport and logistics | Lumps | 1